## Slide 1: An approach to modeling linear and non-linear self-shading losses with pvlib
Will Hobbs1, Kevin Anderson2, Mark Mikofski3, Madison Ghiz3
1Southern Company, 2Sandia, 3DNV
2024 PV Performance Modeling Workshop, May 6, 2024

## Slide 2: Self-shade (row-to-row shade)
About 40% of US utility-scale solar has self-shade losses
  25% thin-film tracking
  18% fixed tilt
    2/3 crystalline  12% of solar has non-linear losses
How do we model all of this?
Non-linearity
Twin modules (w/ half-cut cells)?
Fractional backtracking?
Tracker issues?
Linear
Non-Linear
Non-Linear
Solar stats: Berkely Lab, Utility-Scale Solar 2023, at https://emp.lbl.gov/utility-scale-solar/
Thin-film
Crystalline
Crystalline, twin

## Slide 3
For example…

## Slide 4: Easy to model:
Fixed crystalline w/ no shade

## Slide 5: Hard to model
Lower sun elevation = shade
Non-linear losses
2P, 2P twin, etc…

## Slide 6
What does this look like for power?

## Slide 7: Overestimation at low sun angles:

## Slide 8
Solution using pvlib

## Slide 9: Steps:
Calculate shaded fraction
Calculate power loss
Done!
* Start with array shaded fraction, then calculate for each “course” (i.e., string) of modules
** actually, effective irradiance instead of power loss
*
**

## Slide 10: Shaded Fraction
Use shaded_fraction_front from infinite_sheds.get_irradiance() for array shaded fraction
Then calculate shaded fraction in each course
* For our model, each string can only be in one course
Shade
End view of 3P system (2 rows)
Course 2
Course 1
Course 0
Shaded fraction
Top-down view of 3P system (2 rows)
Course 2
Course 1
Course 0
String 0
String 2
String 1
*

## Slide 11: Twin modules?
Double the number of effective modules up the side of a row
For example, 2P twin  4P effective

## Slide 12: Calculate power (effective irradiance) loss
Thin-film? Loss of direct irradiance linear with shaded fraction, fs
Crystalline? Loss of direct irradiance across the first row of cells
fs = 1/2
POAdirect reduced by 1/2
fs = 1/24
POAdirect reduced by 1/2
Thin-film (linear):
Crystalline (non-linear):
Anderson, Kevin. 2020. Maximizing Yield with Improved Single-Axis Backtracking on Cross-Axis Slopes: Preprint. Golden, CO: National Renewable Energy Laboratory. NREL/CP-5K00-76023. https://www.nrel.gov/docs/fy20osti/76023.pdf.
(and treat twin modules as 2 modules)
(For module with 12 cells up the long axis)
fs ≥ 1/12
POAdirect reduced by 100%

## Slide 13
Some results
with observations from 2 inverters per plant

## Slide 14
1.6% annual difference (NSRDB)

## Slide 15
8.5% annual difference (NSRDB)

## Slide 16
1.9% annual difference (NSRDB)

## Slide 17
2.5% annual difference (NSRDB)

## Slide 18
2.7% annual difference (NSRDB)

## Slide 19
2.3% annual difference (NSRDB)

## Slide 20
Back to the 2P twin plant
let’s look at GCR

## Slide 22
Let’s look at the steps
zoom in on the morning

## Slide 26
Other applications
fractional backtracking, backtracking faults

## Slide 27: Fractional Backtracking
For twin modules, especially 2P (effectively 4P conventional) backtracking to allow shade for a fraction of the array might make sense (maybe even truetracking)
Let’s model a 2P twin example:
🤷
Mode | Annual Energy kWh (NSRDB)
Full backtracking (1.0) | 2058
0.75 backtracking | 2050
0.5 backtracking | 2046
0.25 backtracking | 2044
0.0 (truetracking) | 2043

## Slide 28: Misaligned trackers (clock drift)
Tracker clock is 10 minutes fast
1P 72-cell crystalline
~5% annual losses! (NSRDB)

## Slide 29
Code availability
it’s open-source!

## Slide 30
https://github.com/williamhobbs/2024_pvpmc_self_shade
Repo includes everything shown here:
Functions
example notebooks with plots
anonymized observation data and specs

## Slide 31: Functions
shade_fractions(fs_array, eff_row_side_num_mods)
non_linear_shade(n_cells_up, fs, fd)
plant_power_with_shade_losses(
resource_data,
**plant_data,
surface_tilt_timeseries,
surface_azimuth_timeseries,
use_measured_poa,
use_measured_temp_module)
(https://github.com/williamhobbs/pv-plant-specifications)

## Slide 32: Questions? whobbs@southernco.com
https://github.com/williamhobbs/2024_pvpmc_self_shade