## Slide 1: An approach to modeling linear and non-linear self-shading losses with pvlib
Will Hobbs1, Kevin Anderson2, Mark Mikofski3, Madison Ghiz3
1Southern Company, 2Sandia, 3DNV
2024 PV Performance Modeling Workshop, May 6, 2024

## Slide 2: Self-shade (row-to-row shade)
About 40% of US utility-scale solar has self-shade losses
  25% thin-film tracking
  18% fixed tilt
    2/3 (12% of solar) crystalline  has non-linear losses
How do we model all of this?
Non-linearity
Twin modules (w/ half-cut cells)?
Fractional backtracking?
Tracker issues?
Linear
Non-Linear
Non-Linear
Solar stats: Berkely Lab, Utility-Scale Solar 2023, at https://emp.lbl.gov/utility-scale-solar/
Thin-film
Crystalline
Crystalline, twin

## Slide 3
For example…

## Slide 4: Easy to model:
Fixed crystalline w/ no shade

## Slide 5: Hard to model
Lower sun elevation = shade
Non-linear losses
2P, 2P twin, etc…

## Slide 6
What does this look like for power?

## Slide 7: Overestimation at low sun angles:

## Slide 8
Solution using pvlib

## Slide 9: Steps:
Calculate shaded fraction
Calculate power loss
Done!
* Start with array shaded fraction, then calculate for each “course” (i.e., string) of modules
** actually, effective irradiance instead of power loss
*
**

## Slide 10: Shaded Fraction
Use shaded_fraction_front from infinite_sheds.get_irradiance() for array shaded fraction
Then calculate shaded fraction in each course
* For our model, each string can only be in one course
Shade
End view of 3P system (2 rows)
Course 2
Course 1
Course 0
Shaded fraction
Top-down view of 3P system (2 rows)
Course 2
Course 1
Course 0
String 0
String 2
String 1
*

## Slide 11: Twin modules?
Double the number of effective modules up the side of a row
For example, 2P twin  4P effective

## Slide 12: Calculate power (effective irradiance) loss
Thin-film? Loss of direct irradiance linear with shaded fraction, fs
Crystalline? Loss of direct irradiance across the first row of cells
fs = 1/2
POAdirect reduced by 1/2
fs = 1/24
POAdirect reduced by 1/2
Thin-film (linear):
Crystalline (non-linear):
Anderson, Kevin. 2020. Maximizing Yield with Improved Single-Axis Backtracking on Cross-Axis Slopes: Preprint. Golden, CO: National Renewable Energy Laboratory. NREL/CP-5K00-76023. https://www.nrel.gov/docs/fy20osti/76023.pdf.
(and treat twin modules as 2 modules)
(For module with 12 cells up the long axis)
fs ≥ 1/12
POAdirect reduced by 100%

## Slide 13
Some results
with observations from 2 inverters per plant

## Slide 14
1.6% annual difference (NSRDB)

## Slide 15
8.5% annual difference (NSRDB)

## Slide 16
1.9% annual difference (NSRDB)

## Slide 17
2.5% annual difference (NSRDB)

## Slide 18
2.7% annual difference (NSRDB)

## Slide 19
2.3% annual difference (NSRDB)

## Slide 20
Back to the 2P twin plant
let’s look at GCR

## Slide 22
Let’s look at the steps
zoom in on the morning

## Slide 26
Other applications
fractional backtracking, backtracking faults

## Slide 27: Fractional Backtracking
For twin modules, especially 2P (effectively 4P conventional) backtracking to allow shade for a fraction of the array might make sense (maybe even truetracking)
Let’s model a 2P twin example:
🤷
Mode | Annual Energy kWh (NSRDB)
Full backtracking (1.0) | 2058
0.75 backtracking | 2050
0.5 backtracking | 2046
0.25 backtracking | 2044
0.0 (truetracking) | 2043

## Slide 28: Misaligned trackers (clock drift)
Tracker clock is 10 minutes fast
1P 72-cell crystalline
~5% annual losses! (NSRDB)

## Slide 29
Code availability
it’s open-source!

## Slide 30
https://github.com/williamhobbs/2024_pvpmc_self_shade
Repo includes everything shown here:
Functions
example notebooks with plots
anonymized observation data and specs

## Slide 31: Functions
shade_fractions(fs_array, eff_row_side_num_mods)
non_linear_shade(n_cells_up, fs, fd)
plant_power_with_shade_losses(
resource_data,
**plant_data,
surface_tilt_timeseries,
surface_azimuth_timeseries,
use_measured_poa,
use_measured_temp_module)
(https://github.com/williamhobbs/pv-plant-specifications)

## Slide 32: Questions? whobbs@southernco.com
https://github.com/williamhobbs/2024_pvpmc_self_shade

## Slide 33: Room for improvement
Account for “inactive bands” at module edges (or, at least, see how much it matters)
Crystalline modules in landscape
Unconventional crystalline module designs (shingled cells, etc.)
Comparison with single diode model
Slopping terrain (https://github.com/pvlib/pvlib-python/pull/1962 by echedey-ls will help)
isotropic looks better than haydavies, even in periods with no direct shade – why?